## Bidding
|  |  | BIDDING: CONTRACTOR RFI | RFI LOG / RESPONSES
Project Name: | Boyce Biology Lab Renovation
Number: | CCAC-006
Submittal Received Date: |  | 2025-11-26
Submittal Dated: |  | 2025-12-18
Design Phase: |  | 15% SD1
Design Phase | Date Comment Received by AE Works | Discipline | Description | RFI Question | AE Response | AE Response Date | A/E Reviewer | CCAC Comments
BIDDING | 2026-04-22 | CCAC / Architecture | Existing Roof Warranty | Is the existing roof under warranty? Who is the Manufacturer? Do you know who was the original installer? | The information is unavailable. The existing roof will be patched and then replaced as noted in the contract documents. | 2026-04-29 | Architecture (FS) CCAC (MP)
BIDDING | 2026-04-28 | CCAC / Architecture | Demolition | Does each trade own their own demolition? Dumpsters? | Each contractor is responsible for demolition as detailed in the contract documents. GC shall provide 3 dumpsters during demolition for use by all prime contractors. GC may reduce to 1 dumpster after demolition depending on overall need. | 2026-04-29 | Architecture (FS) CCAC (DD)
BIDDING | 2026-04-28 | Architecture | EIL Insurance | For the Environmental Impairment Liability requirement, has any site-specific environmental testing been completed? How many years, following completion, will the EIL insurance need to be carried? | The environmental report was provided in Addendum 01. EIL insurance shall be carried for 10 years. | 2026-04-30 | Architecture (FS) CCAC (MG)
BIDDING | 2026-04-29 | CCAC / Architecture | Existing Roof Warranty | Please provide the existing roof warranty information for this project, if available. If no existing roof warranty is in place, please confirm. | The information is unavailable. The existing roof will be patched and then replaced as noted in the contract documents. | 2026-04-29 | Architecture (FS)
BIDDING | 2026-04-30 | Architecture | Lab Fixture Finish | Specification section 123553, item 2.8.A.2 indicates that the fixtures are to have a Sepia Bronze finish when specified. However, per section 224010, item 2.2.A.2.b indicates that fixtures are to be chrome plated. Please clarify that Watersaver standard polished chrome finish is acceptable for the fixtures on this project. | Provide the Watersaver standard polished chrome finish. | 2026-05-04 | Architecture (FS)
BIDDING | 2026-04-30 | Architecture | Lab Benches | The details for the student benches in the labs, SB-1A/B and SB-2A/B do not provide any information as to what the difference is between the lab benches. Also both benches are indicated to have either sink type 1, 3, or 6 at them. Per drawing A404, sink types 1, 3, and 6 are identical sink sizes. When viewing the lab drawings on A401 and A402, the student benches SB-1B and SB-2A appear to have smaller sinks. Please clarify if these benches require a different sink size than what is indicated on drawing A404. | Lab bench types 1B and 2B have an ADA compliant apron in lieu of a sink base cabinet as noted on bench types 1A and 2A. Follow the sink type sizes noted on A404. Each type includes different boring locations and accessories (eyewash and DI faucet) | 2026-05-04 | Architecture (FS)
BIDDING | 2026-04-30 | Architecture | Casework Specifications | There are some items that do not appear to have any specification associated with them. These are the plastic laminate cubbies that are in each lab, detail 6/A501, and the upholstered built in benches, detail 4/A501. Please provide a specification for these items. | See specification section 12 64 13 BOOTHS for built-in bench. New specification section 06 40 23 INTERIOR ARCHITECTURAL WOODWORK and revised A501 drawing included in Addendum | 2026-05-05 | Architecture (FS)
BIDDING | 2026-04-30 | Electrical | Multiple Items | 1) Drawing E601 indicates an existing distribution panel #3 feeding DOAS-1, please indicate the panel manufacturer so we can purchase the new 70A breaker required 2) Drawing E601 indicates an existing distribution panel #2 feeding new panels E and D, please indicate the panel manufacturer so we can purchase the new 150A breaker required 3) There is a VFD indicated on E601, where is this located in relation to DOAS-1. Also, who provides and installs the VFD 4) The Fire Alarm system appears to be a Siemens system, can you tell me where the main fire alarm panel is located. Please provide make and model, and who services the system 5) Drawing E602 indicates an existing panel ‘N’ feeding EF-1 and EF-2, please indicate the panel manufacturer so we can purchase the new 20A breaker required 6) Please indicate on the floor plan where existing distribution panels #2 and #3 are located in order to calculate the correct footage for the feeders required 7) Drawing E201 number note 1, please provide a manufacture and catalog number for the poke throughs required for connection points in the lab benches | 1) Field verify in construction. 2) Manufactuer is GE 3) The VFD is provided by the EC. Install on the DOAS with a NEMA 4X enclosure or provide an outdoor rated VFD. 4) The main panel is located on the first floor of the north wing in switchgear room N117. 5) Manufacturer is GE 6) Distribution panel #2 is located in room 416 and Distribution panel #3 is located in room 549. Refer to floor plans provided in Addendum. | 2026-05-07 | Electrical (TD)
BIDDING | 2026-05-01 | Plumbing | Acid Waste and Vent | The current Division 22 - Plumbing spec section does not include the specification for Acid Waste and Vent. Please provide | Section 221300 will be added in addendum | 2026-05-04 | Plumbing (SW)
BIDDING | 2026-05-01 | Plumbing | DI Water | What is the PPM of TDS of the incoming water? How much water will be used daily or weekly? | TDS of incoming water not specified. Contractor to verify via local utility data or field testing. Typical range: 150-300 PPM. Provide Grade 3 water quality. DI water is required at the locations noted in the documents. | 2026-05-04 | Plumbing (SW)
BIDDING | 2026-05-01 | Electrical | Conduit
BIDDING | 2026-05-01 | CCAC | 5th Floor Above Ceiling Work | At the pre-bid it was mentioned that work on the fifth floor was to take place during off-hours.Will this space be occupied during summer months?If so, would this work be required on 3rd shift or weekends? | The scheduling of the work will be coordinated with the contractor(s) once they are on board. | 2026-05-06 | CCAC (NK)
BIDDING | 2026-05-01 | Electrical / LV | Electrical Room Locations
BIDDING | 2026-05-01 | Electrical / LV | Security Devices | Who is supplying the security devices for the project? | LV: See drawing E301, Communications General Note 10 and 11 - The contractor is to provide security devices. | 2026-05-05 | Low-V: DS
BIDDING | 2026-05-01 | Electrical | Light Fixtures
BIDDING | 2026-05-01 | Electrical | Light Fixtures
BIDDING | 2026-05-01 | Electrical / LV | Security Systems
BIDDING | 2026-05-01 | Electrical / LV | Security Cabling | Can a spec for security cabling be added? | LV: See drawing E301, Communications General Note 11, The Contractor is responsible for evaluating existing conditions and finalize requirements. | 2026-05-05 | Low-V: DS
BIDDING | 2026-05-01 | Architecture | Coordination of Work | It was stated at the pre-bid that the GC was responsible for removing and replacing ceiling tile on the 5th floor for work above ceiling. Can it be confirmed it is GC's responsibility for ceiling tile and for the dust containment enclosure for this work? | Refer to General Coordination Notes on AD102: Each contractor is responsible for removal and replacement of existing ceiling tiles and fixtures as required to perform wok. The GC is responsible for the dust containment enclosure at each phase of work. In addition to drawing notes, each contractor is responsible for any required patching and firestopping as a result of their own work. | 2026-05-04 | Architecture (FS)
BIDDING | 2026-05-01 | Electrical | Floor Outlet | On drawing E401 detail 6 it shows a poke through detail. Can a manufacturer and model number be provided to match owner/architect intent? | Proivde Wiremold RC7AFFTCAL poke-thru | 2026-05-04
BIDDING | 2026-05-01 | Electrical / Mechanical | Occupancy Sensors for Lab Air | On drawing E101 Note 6 it refers to ceiling occ sensors to control lab air. Is the intent to add a power pack and controls in each lab to accomplish this? | Yes, the intent is to be able to control each room independently of the other. | 2026-05-04
BIDDING | 2026-05-01 | Electrical | Add Alternate
BIDDING | 2026-05-01 | Architecture | Demolition Scope | Is GC or Plumber responsible for demo of plumbing in classrooms? Same for Electric & HVAC Duct. | Each contractor is responsible for demolition as detailed in the contract documents. | 2026-05-04 | Architecture (FS)
BIDDING | 2026-05-01 | CCAC | Freight Elevator | Is there a freight elevator available for Contractor use? | No freight elevator. Use passenger elevator in south wing or use a lift to a window within the lab space. | 2026-05-05 | CCAC (MP)
BIDDING | 2026-05-01 | CCAC | Sign-In Sheets | Please provide a copy of sign in sheets. | Sign in sheets provided in Addendum 01 on 05/01/2026 | 2026-05-01 | CCAC
BIDDING | 2026-05-01 | CCAC / Electrical | LV Bids | Are Low Voltage bids going to the Electrical Contractors? | Yes, low voltage is in the Electrical Contractor's scope of work. | 2026-05-05 | Architecture (FS)
BIDDING | 2026-05-01 | Electrical / LV | TR Room Location
BIDDINGA38:J38 | 2026-05-01 | CCAC / Electrical / LV | Data Racks
BIDDING | 2026-05-01 | CCAC / LV | LV Cable Type
BIDDING | 2026-05-01 | Electrical | Add Alternate Single Line Diagram | In reference to the alternate for this project, can a single line diagram be issued on how we are to wire the key switches, it appears that there are 15 circuits which would need a shunt trip breaker for each receptacle circuit involved at the panels. Would we need a keyed switch for each circuit? | Each room will be controlled individually so there would be one key switch controlling multiple contactors (either one for each circuit or multi-poke contactors with separate contact sets). | 2026-05-04 | Electrical (TD)
BIDDING | 2026-05-01 | Mechanical | Existing Risers | Drawing M-111, we are tying into existing risers do you know what size they are? The first branch off is an unknown size and they look as if they are going down, can you verify please? | It depends where it is deemed possible to connect to the largest mains in the mechanical room, and the branch off is (4) 1-1/4" drain lines. | 2026-05-05 | Mech (BG)
BIDDING | 2026-05-04 | CCAC | Staging | Where will our lay down area be located? Where will we be able to stage a dumpster? Is there a freight elevator that will be available to contractors? | Dumpsters and laydown area per attached document from CCAC Facilities. No freight elevator exists. Use passenger elevator in south wing or use a lift to a window within the lab space. | 2026-05-05 | CCAC (MP)
BIDDING | 2026-05-04 | Architecture | 5th Floor Above Ceiling Work | Which trade will be responsible for the ACT removal and replacement on the Fifth Floor? Will containments be required and if so who is responsible for their construction and maintenance? | Refer to General Coordination Notes on AD102: Each contractor is responsible for removal and replacement of existing ceiling tiles and fixtures as required to perform wok. The GC is responsible for the dust containment enclosure at each phase of work. In addition to drawing notes, each contractor is responsible for any required patching and firestopping as a result of their own work. | 2026-05-04 | Architecture (FS)
BIDDING | 2026-05-04 | LV / Electrical | Cables | How many cables to a half shaded triangle? | Refer to outlet details on E404 | 2026-05-05 | Low-V: DS
BIDDING | 2026-05-04 | Mechanical / Plumbing | Ceiling Plenum | Is the ceiling of the fifth and sixth floors return air plenum? If the ceiling of the sixth floor is return air plenum, which specification do we use for the DI Water system | The 6th floor does not have a return plunum. The 5th floor is unknown. | 2026-05-05 | Mech (BG)
BIDDING | 2026-05-04 | CCAC | MBE / WBE Requirement | Page 15/732 states a goal of 15% MBE/WBE. Page 26/732 ( General Conditions para 6) states a goal of 13% MBE & 7% WBE. Which goal is correct? | The 20% goal is applicable – 13% MBE and 7% WBE. | 2026-05-04 | CCAC Mike Cvetic
BIDDING | 2026-05-04 | Architecture | Classroom Board Install | On drawing E502 there are several items that are owner furnished contractor installed including 4x4 ceramic white boards, 6x4 ceramic white boards, and 86" Interactive displays. Whose responsibility is it to install these items the GC or EC? | GC shall install the Interactive displays and white boards. The EC shall provide all necessary power and data for a complete installation. | 2026-05-05 | Architecture (FS)
BIDDING | 2026-05-04 | Electrical | Distribution Panel | PLEASE PROVIDE EITHER A LOCATION DRAWING OR THE DISTANCE FOR THE NEW FEEDERS COMING FROM DISTRIBUTION PANEL #2 TO THE NEW PANELS D & E | Distribution panel #2 is located in room 416. Refer to floor plans provided in Addendum. | 2026-05-06 | Architecture (FS)
BIDDING | 2026-05-04 | Electrical | Distribution Panel | PLEASE PRODIVE EITHER A LOCATION DRAWING OR THE DISTANCE FOR THE NEW FEEDER COMING FROM DISTRIBUTION PANEL #2 TO DOAS-1 | Distribution panel #2 is located in room 416. Refer to floor plans provided in Addendum. | 2026-05-06 | Architecture (FS)
BIDDING | 2026-05-04 | Electrical | Fire Alarm Vendor
BIDDING | 2026-05-04 | Electrical | MC Cable
BIDDING | 2026-05-04 | Electrical | MC Cable
BIDDING | 2026-05-04 | Electrical | Emergency Lighting
BIDDING | 2026-05-04 | Electrical | Equipment
BIDDING | 2026-05-04 | Architecture | Furred Walls | THERE WAS MENTION AT THE WALK THRU THAT THE WALLS IN FRONT OF PANELS E & D WILL BE FURED OUT FOR THE INSTALLATION OF THE NEW PANELS E&D THAT ARE BEING INSTALLED. CAN THAT PLEASE BE CONFIRMED? | New panels are in same location as existing panels.No wall furring is included at this time. | 2026-05-05 | Architecture (FS)
BIDDING | 2026-05-04 | CCAC/Architecture | Phasing | WILL THE LABS BE FULLY SHUT DOWN DURING CONSTRUCTION? | The labs will be unoccupied during construction. Refer to sheet G102 for project phasing, access requirements to existing toilet rooms, corridor, and stairs. | 2026-05-05 | Architecture (FS)
BIDDING | 2026-05-04 | CCAC | 5th Floor Above Ceiling Work | GENERAL NOTE #3 UNDERFLOOR WORK. STATES THAT ALL WORK UNDERFLOOR IS THE BE SCHEDULED ON SUMMER BREAKS, HOLIDAYS & OR WEEKENDS. CAN YOU PLEASE PROVIDED WHEN THE SCHOOL BREAKS BEGIN AND END AS WELL AS ANY HOLIDAYS THAT WERE MENTINONED | The scheduling of the work will be coordinated with the contractor(s) once they are on board. | 2026-05-06 | CCAC (NK)
BIDDING | 2026-05-04 | CCAC | MBE / WBE Requirement | THE BID FORM 1148 ELECTRICAL MBE/WBE PARTICIPATION STATES 15% WHEREAS GENERAL CONDITIONS PARAGRAPH 6 STATES 20% 13% MINORITY & 7% WOMAN. CAN YOU PLEASE CLAIRFY WHICH ONE IS CORRECT? | The 20% goal is applicable – 13% MBE and 7% WBE. | 2026-05-05 | CCAC (MC)
BIDDING | 2026-05-04 | Electrical | Light Fixtures
BIDDING | 2026-05-04 | CCAC / Mechanical | DDC System | It says that a JCI Metasys is the only accepted DDC manufacture/system. Would CCAC be willing to accept ALC as an alternative if we could integrate back into the existing JCI system using BACnet? *Clarification Request: On Sheet 230923-36, Spec Sec. 3.2, It says "DDC System Interface with Existing Siemens BAS." Is the existing system in fact Siemens or is it JCI Metasys? | Existing System is JCI Metasys, and the owner has instructed us not to allow alternates. | 2026-05-05 | Mech (BG)
BIDDING | 2026-05-05 | Electrical | Fire Alarm Symbols
BIDDING | 2026-05-05 | CCAC | Bonds | 1. Project start and finish dates June 2026 through substantial completion 4-2-27. 2. Any Maintenance Period 3. Liquidated Damages/Penalties | 1) June 2026 through substantial completion 4-2-27. 2) N/A 3) There are liquidated damages in the A101 of $500 per day. | 2026-05-05 | CCAC (MC)
BIDDING | 2026-05-05 | Electrical | Liquidated Damages | Is there any Liquidated Damages for this project? | There are liquidated damages in the A101 of $500 per day. | 2026-05-05 | CCAC (MC)
BIDDING | 2026-05-05 | Architecture | Floor-to-Floor Heights | What is the existing floor-to-deck height within the area(s) scheduled to be renovated? | The roof deck is approximately 14'-8" above the 6th floor level. Verify in field | 2026-05-05 | Architecture (FS)
BIDDING | 2026-05-05 | Architecture | 5th Floor Above Ceiling Work | The fifth floor plumbing demo/installation will require the ACT ceilings to be opened for access. During the pre-bid meeting walk through it was stated that the GC will be resposible for the removal and replacement of the ACT ceilings for the plumbing and electrical work on the fifth floor. Can you please verify that this work will be required to be done by the GC. | Refer to General Coordination Notes on AD102: Each contractor is responsible for removal and replacement of existing ceiling tiles and fixtures as required to perform wok. The GC is responsible for the dust containment enclosure at each phase of work. In addition to drawing notes, each contractor is responsible for any required patching and firestopping as a result of their own work. | 2026-05-05 | Architecture (FS)
BIDDING | 2026-05-05 | Architecture | Fixture Scope | Under the GC Summary, it states "GC to provide laboratory casework and associated plumbing fixtures, Installation of associated plumbing fixtures by Plumbing Contractor". On drawing P001, in the plumbing fixture schedule, it shows the PC is to provide the faucets for the S-1 & S-2. Please confirm that the GC is to provide and install the counter top (with integral sink bowl) and the PC is to provide and install the faucets and additional items mentioned in the plumbing fixture schedule. | GC shall purchase the lab sinks and faucets as part of the lab casework package. The GC shall install the sink with the lab countertops. The PC shall provide all components not included in the casework package and shall install all faucets, drains, plumbing lines, and any remaining components necessary for a complete system. | 2026-05-06 | Architecture (FS)
BIDDING | 2026-05-05 | Plumbing | Acid Waste and Vent | Under the sanitary waste and vent piping, there are no specifications for the acid waste and acid vent piping. Can you please add these specifications to the next addendum? | Section 221300 will be added in addendum | 2026-05-04 | Plumbing (SW)
BIDDING | 2026-05-05 | Plumbing | DI Water | Under the Processed Water Systems section there are no specifications for the DI System equipment. Is the equipment being supplied by others (CCAC) or the PC? If by the PC, can you distribute the specifications in the next addendum? Also, if it is being supplied by others, will the PC be expected to install it? | The DI system is a delegated design and shall be provided by the PC. Provide Type III DI water for the locations noted in the documents. | 2026-05-07 | Plumbing (SW)
BIDDING | 2026-05-05 | Electrical / LV | Access Control
BIDDING | 2026-05-05 | Electrical | Lighting Controls
BIDDING | 2026-05-05 | Electrical | Light Fixtures
BIDDING | 2026-05-05 | Electrical | Light Fixtures
BIDDING | 2026-05-05 | Electrical | Emergency Lighting
BIDDING | 2026-05-05 | Electrical | Panel
BIDDING | 2026-05-05 | Electrical | Panel Location | Please provide location of distribution panels #2 and #3. | Distribution panel #2 is located in room 416 and Distribution panel #3 is located in room 549. Refer to floor plans provided in Addendum. | 2026-05-06 | Architecture (FS)
BIDDING | 2026-05-05 | Electrical | IT Location | Please provide location of IT room. | Refer to attached plans for server room location. | 2026-05-06 | Architecture (FS)
BIDDING | 2026-05-05 | Electrical | Lighting Controls
BIDDING | 2026-05-05 | Electrical | Lighting Panel Location
BIDDING | 2026-05-05 | CCAC | Labor Participation | The Project Labor Agreement requires the general contractor and all subcontractors to provide only union labor for this project, effectively preventing non-union contractors from bidding or working on the project, which limits the pool of MWDBE companies able to participate on this project. Though the Labor Stabilization Agreement states non-union contractors can be used on the project, they will have to work with the union and provide union labor, essentially signing on with the union. Please confirm this will be taken into consideration when reviewing good faith efforts in case of the event that the participation goals cannot be attained. Additionally, there are contradicting participation goals in the spec. Return Form 4.0 states 15% overall but section 6 of the General Conditions states 20%. Please advise which is correct. | The 20% goal is applicable – 13% MBE and 7% WBE. |  |  | This will be taken into consideration when evaluating the good faith effort. Also, be reminded that the purchase of supplies/materials used for the project from MWDBE firms will be considered. Part 2 pertains to the percentage (15% vs. 20%). The correct one is 20%.
BIDDING | 2026-05-06 | Electrical | Panel Location | 1. E602 - Please provide a floor plan showing locations of DIST. PANEL #2 and DIST PANEL #3. This is necessary to assess the feeders to the new panels (D and E) and to DOAS-1. | Distribution panel #2 is located in room 416 and Distribution panel #3 is located in room 549. Refer to floor plans provided in Addendum. | 2026-05-06 | Architecture (FS)
BIDDING | 2026-05-06 | Low Voltage | Data Cables
BIDDING | 2026-05-06 | Low Voltage | TR Room Location
BIDDING | 2026-05-06 | Low Voltage | Cabling
BIDDING | 2026-05-06 | Low Voltage | Security
BIDDING | 2026-05-06 | LV / Electrical | Floor Outlet
BIDDING | 2026-05-06 | Electrical | Panel Conduits
BIDDING | 2026-05-06 | Electrical | Feeders / Raceway
BIDDING | 2026-05-06 | Electrical | Spares Locations
BIDDING | 2026-05-06 | Electrical | DOAS Label
BIDDING | 2026-05-06 | Electrical | Light Fixtures
BIDDING | 2026-05-06 | Electrical | Wattstopper
BIDDING | 2026-05-06 | CCAC | Schedule | PLEASE PROVIDE START AND DURATION FOR THE PROJECT. | June 2026 through substantial completion 4-2-27. | 2026-05-06 | CCAC (MC)
BIDDING | 2026-05-06 | CCAC | Bid Extension | WE ARE REQUESTING AN EXTENSION OF THE BID DATE DUE TO THE NUMBER OF THE QUESTIONS WE HAVE AND TO GIVE US ADEQUATE TIME AFTER RFI'S ARE ANSWERED TO IMPLEMENT RESPONSES. |  |  |  | The due date has been extended to Friday, May 15, 2026 at 2:00 p.m.
BIDDING | 2026-05-06 | Mechanical | Panels | Are perforated panels required for fan sections only, or every section in the unit? | Perforated panels are required for all sections of the DOAS. | 2026-05-07 | Mech (TC)
BIDDING | 2026-05-06 | Mechanical | Coating | Could you please provide more information on the microbial coating requirement for the inside casing wall? | Strike specifications section 2.3 C. 2. c. from the requirements of the DOAS. The antimicrobial coating will NOT be required. | 2026-05-07 | Mech (TC)
BIDDING | 2026-05-06 | Mechanical | Unit Dimensions | Could you please advise on the max weight, length, and height of the unit? | Refer to the Dedicated Outdoor Air System schedule on M702 for max size and weight. | 2026-05-07 | Mech (TC)
BIDDING | 2026-05-06 | Mechanical | Supply Fans | Please advise on the number of supply fans. | 2 supply fans in the DOAS. | 2026-05-07 | Mech (TC)
BIDDING | 2026-05-06 | Mechanical | Bypass Dampers | Are internal bypass dampers acceptable in lieu of integral bypass dampers? | Internal bypass dampers will be an acceptable substitution for IFB dampers | 2026-05-07 | Mech (TC)
BIDDING | 2026-05-06 | Mechanical | Unit Orientation | What is the orientation of DOAS-1? The plans show vertical, but the spec states horizontal. | Horizontal. | 2026-05-07 | Mech (TC)
BIDDING | 2026-05-06 | Mechanical | Unit Layout | Could a detailed layout of DOAS-1 be provided? | No addendum will be provided. Please follow the DOAS schedule and specifications section 237433 for specific requirements of the DOAS. | 2026-05-07 | Mech (TC)
BIDDING | 46148 | Mechanical | Exhaust Ductwork | The sheet metal material spec says to use 316 SS for ductwork connected to fume hoods. The duct specs do not indicate if the indoor fume hood duct should have welded joints. Please advise if the fume hood exhaust duct should have welded or flanged joints. | Please include welded joints for fume hood exhaust | 2026-05-06 | Mech (BG)
BIDDING | 2026-05-07 | Architecture | Dust Enclosures | General Coordination Note #3 & 4 - All primes to provide a phasing plan for approval. General Contractor to provide dust protection for work by the primes on the 5th floor for each phase. As a General Contractor, how are we to know how large of an area that we need protection to provide for each phase when the phases have not been determined yet? We'll have to install and take down for each phase. How many phases are we to include? | The work will have to be planned between the Prime Contractors and CCAC as stated in the contract documents. | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 | Architecture | Coordination of Work | Who is responsible for coordination between trades? In one section is says the owner will be responsible but in the General Construction scope it lists coordination between trades as being on the GC. | The GC is responsible for coordination of trades. | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 | Low Voltage | Cable Demoliton
BIDDING | 2026-05-07 | Architecture | OFCI Equipment
BIDDING | 2026-05-07 | CCAC | Award Date
BIDDING | 2026-05-07 | CCAC | Start Date | What is the anticipated start date? | 2026-06-01 | 2026-05-07 | CCAC (MC)
BIDDING | 2026-05-07 | Architecture | New Roof | What type of roofing system will be installed during the upcoming roof replacement project? | Refer to Roof Plan on sheet A121 | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 | CCAC | New Roof Install | When is the new roofing system anticipated to be installed? | Concurrent with this project | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 | Architecture | Schedule | Section 13200 B. Related Requirements: states Reference Section 011000 “Summary" for preparing a combined Contractor's Construction Schedule. Section 011000 has references to the contractor preparing schedules but does not appear to have anything referencing a combined schedule. Who is responsible for creating a combined schedule? | The GC is responsible. | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 | CCAC | Laydown Area | Where will the contractors be allowed to have their laydown yard for dumpster and materials staging? | Refer to attached plan from CCAC. | 2026-05-07 | CCAC (MC)
BIDDING | 2026-05-07 | Architecture | Roof Walkway Pads | Sheet A121 Construction Key Note 7.08 states “Provide new Membrane Walkway Pads, Adhered to Roof Membrane”. During the walkthrough it was noted that this work would likely be done before the new roof was completed. Please confirm if the contractors bidding should provide these or if the contractor installing the new roof will be providing the walkway pads? | Refer to General Note 6 on sheet A121. | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07
BIDDING | 2026-05-07
BIDDING | 2026-05-07
BIDDING | 2026-05-07 |  |  | Is the Electrical contractor responsible to install the display monitors and the associated mounting hardware? | GC shall install the Interactive displays. The EC shall provide all necessary power and data for a complete installation. | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 |  |  | Will the GC furnish wall blocking where required for display mounting? | GC will furnish blocking per notes on A401 and A402 | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 |  |  | Which prime is responsible for mounting the whiteboards listed in the OFCI Schedule on E502? Can you provide a breakdown of which prime is responsible for each of the OFCI items? | GC shall install the white boards. | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07
BIDDING | 2026-05-07 | Electrical | Fire Alarm Devices
Electrical | 2026-05-07 | Electrical | Fire Alarm System
.