## Bidding
|  |  | BIDDING: CONTRACTOR RFI | RFI LOG / RESPONSES
Project Name: | Boyce Biology Lab Renovation
Number: | CCAC-006
Design Phase: |  | BIDDING
Design Phase | Date Comment Received by AE Works | Discipline | Description | RFI Question | AE Response | AE Response Date | A/E Reviewer | CCAC Comments
BIDDING | 2026-04-22 | CCAC / Architecture | Existing Roof Warranty | Is the existing roof under warranty? Who is the Manufacturer? Do you know who was the original installer? | The information is unavailable. The existing roof will be patched and then replaced as noted in the contract documents. | 2026-04-29 | Architecture (FS) CCAC (MP)
BIDDING | 2026-04-28 | CCAC / Architecture | Demolition | Does each trade own their own demolition? Dumpsters? | Each contractor is responsible for demolition as detailed in the contract documents. GC shall provide 3 dumpsters during demolition for use by all prime contractors. GC may reduce to 1 dumpster after demolition depending on overall need. | 2026-04-29 | Architecture (FS) CCAC (DD)
BIDDING | 2026-04-28 | Architecture | EIL Insurance | For the Environmental Impairment Liability requirement, has any site-specific environmental testing been completed? How many years, following completion, will the EIL insurance need to be carried? | The environmental report was provided in Addendum 01. EIL insurance shall be carried for 10 years. | 2026-04-30 | Architecture (FS) CCAC (MG)
BIDDING | 2026-04-29 | CCAC / Architecture | Existing Roof Warranty | Please provide the existing roof warranty information for this project, if available. If no existing roof warranty is in place, please confirm. | The information is unavailable. The existing roof will be patched and then replaced as noted in the contract documents. | 2026-04-29 | Architecture (FS)
BIDDING | 2026-04-30 | Architecture | Lab Fixture Finish | Specification section 123553, item 2.8.A.2 indicates that the fixtures are to have a Sepia Bronze finish when specified. However, per section 224010, item 2.2.A.2.b indicates that fixtures are to be chrome plated. Please clarify that Watersaver standard polished chrome finish is acceptable for the fixtures on this project. | Provide the Watersaver standard polished chrome finish. | 2026-05-04 | Architecture (FS)
BIDDING | 2026-04-30 | Architecture | Lab Benches | The details for the student benches in the labs, SB-1A/B and SB-2A/B do not provide any information as to what the difference is between the lab benches. Also both benches are indicated to have either sink type 1, 3, or 6 at them. Per drawing A404, sink types 1, 3, and 6 are identical sink sizes. When viewing the lab drawings on A401 and A402, the student benches SB-1B and SB-2A appear to have smaller sinks. Please clarify if these benches require a different sink size than what is indicated on drawing A404. | Lab bench types 1B and 2B have an ADA compliant apron in lieu of a sink base cabinet as noted on bench types 1A and 2A. Follow the sink type sizes noted on A404. Each type includes different boring locations and accessories (eyewash and DI faucet) | 2026-05-04 | Architecture (FS)
BIDDING | 2026-04-30 | Architecture | Casework Specifications | There are some items that do not appear to have any specification associated with them. These are the plastic laminate cubbies that are in each lab, detail 6/A501, and the upholstered built in benches, detail 4/A501. Please provide a specification for these items. | See specification section 12 64 13 BOOTHS for built-in bench. New specification section 06 40 23 INTERIOR ARCHITECTURAL WOODWORK and revised A501 drawing included in Addendum | 2026-05-05 | Architecture (FS)
BIDDING | 2026-04-30 | Electrical | Multiple Items | 1) Drawing E601 indicates an existing distribution panel #3 feeding DOAS-1, please indicate the panel manufacturer so we can purchase the new 70A breaker required 2) Drawing E601 indicates an existing distribution panel #2 feeding new panels E and D, please indicate the panel manufacturer so we can purchase the new 150A breaker required 3) There is a VFD indicated on E601, where is this located in relation to DOAS-1. Also, who provides and installs the VFD 4) The Fire Alarm system appears to be a Siemens system, can you tell me where the main fire alarm panel is located. Please provide make and model, and who services the system 5) Drawing E602 indicates an existing panel ‘N’ feeding EF-1 and EF-2, please indicate the panel manufacturer so we can purchase the new 20A breaker required 6) Please indicate on the floor plan where existing distribution panels #2 and #3 are located in order to calculate the correct footage for the feeders required 7) Drawing E201 number note 1, please provide a manufacture and catalog number for the poke throughs required for connection points in the lab benches | 1) Field verify in construction. 2) Manufactuer is GE 3) The VFD is provided by the EC. Install on the DOAS with a NEMA 4X enclosure or provide an outdoor rated VFD. 4) The main panel is located on the first floor of the north wing in switchgear room N117. 5) Manufacturer is GE 6) Distribution panel #2 is located in room 416 and Distribution panel #3 is located in room 549. Refer to floor plans provided in Addendum. | 2026-05-07 | Electrical (TD)
BIDDING | 2026-05-01 | Plumbing | Acid Waste and Vent | The current Division 22 - Plumbing spec section does not include the specification for Acid Waste and Vent. Please provide | Section 221300 will be added in addendum | 2026-05-04 | Plumbing (SW)
BIDDING | 2026-05-01 | Plumbing | DI Water | What is the PPM of TDS of the incoming water? How much water will be used daily or weekly? | TDS of incoming water not specified. Contractor to verify via local utility data or field testing. Typical range: 150-300 PPM. Provide Type II water quality. DI water is required at the locations noted in the documents. | 2026-05-12 | Plumbing (SW)
BIDDING | 2026-05-01 | Electrical | Conduit | In spec. section 260533 part 3.1.A.2 it lists EMT to be used above ceilings and in walls. Is MC acceptable for branch ciurcuit wiring? | MC cable for branch circuit can be used provided it meets appplicable NEC requirements. Coordinate with AHJ for final approval. | 2026-05-04
BIDDING | 2026-05-01 | CCAC | 5th Floor Above Ceiling Work | At the pre-bid it was mentioned that work on the fifth floor was to take place during off-hours.Will this space be occupied during summer months?If so, would this work be required on 3rd shift or weekends? | The scheduling of the work will be coordinated with the contractor(s) once they are on board. | 2026-05-06 | CCAC (NK)
BIDDING | 2026-05-01 | Electrical / LV | Electrical Room Locations | Can drawings with locations of the IDF room and 4th floor electric room be added to the bid set? | LV: See drawing E301, Communications General Note 5 - Coordinate Telecom Room location w/ local CCAC representatives. Refer to attached plans for server room and distribution panel locations. | 2026-05-05 | Low-V: DS
BIDDING | 2026-05-01 | Electrical / LV | Security Devices | Who is supplying the security devices for the project? | LV: See drawing E301, Communications General Note 10 and 11 - The Contractor bidding on the work is to provide security devices. | 2026-05-05 | Low-V: DS
BIDDING | 2026-05-01 | Electrical | Light Fixtures | For the light fixtures that are "Remove and Replace" will there be a designated location on the campus to store light fixtures? | N/A See Addendum 3 | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-01 | Electrical | Light Fixtures | Is it the EC's responsibility to clean existing fixtures? | N/A See Addendum 3 | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-01 | Electrical / LV | Security Systems | On drawing E301 Note 10 it states to inergrate security systems. Where is the existing security room located? Who is responsible for tying into the existing system? | LV: See drawing E301, Communications General Note 10 - Coordinate systems location w/ local CCAC representatives. Per note 10 and 11, The Contractor bidding on the work is responsible for tying into the existing system. CCAC to respond with system Service Provider. | 2026-05-05 | Low-V: DS
BIDDING | 2026-05-01 | Electrical / LV | Security Cabling | Can a spec for security cabling be added? | LV: See drawing E301, Communications General Note 11, The Contractor is responsible for evaluating existing conditions and finalize requirements. | 2026-05-05 | Low-V: DS
BIDDING | 2026-05-01 | Architecture | Coordination of Work | It was stated at the pre-bid that the GC was responsible for removing and replacing ceiling tile on the 5th floor for work above ceiling. Can it be confirmed it is GC's responsibility for ceiling tile and for the dust containment enclosure for this work? | Refer to General Coordination Notes on AD102: Each contractor is responsible for removal and replacement of existing ceiling tiles and fixtures as required to perform wok. The GC is responsible for the dust containment enclosure at each phase of work. In addition to drawing notes, each contractor is responsible for any required patching and firestopping as a result of their own work. | 2026-05-04 | Architecture (FS)
BIDDING | 2026-05-01 | Electrical | Floor Outlet | On drawing E401 detail 6 it shows a poke through detail. Can a manufacturer and model number be provided to match owner/architect intent? | LV: Provide Wiremold RC7AFFTCAL poke-thru for electric. Provide Wiremold poke-thru w/ 1-1/2" raceway for LV. | 2026-05-04
BIDDING | 2026-05-01 | Electrical / Mechanical | Occupancy Sensors for Lab Air | On drawing E101 Note 6 it refers to ceiling occ sensors to control lab air. Is the intent to add a power pack and controls in each lab to accomplish this? | Yes, the intent is to be able to control each room independently of the other. | 2026-05-04
BIDDING | 2026-05-01 | Electrical | Add Alternate | Regarding the add alternate note on drawing E201. In lieu of installing shunt trip breakers, should the receptacle branch power circuitry be controlled via a contractor with remote/key switch operation? This would allow the key switch de-energize and re-energize the circuits while also allowing sufficient space in the panel for circuit breakers. | Yes, contactor with remote/key switch can be used as an option. Obtain final approval from CCAC. Contactos will possibly work bes with untiple circuits being controlled at one time. | 2026-05-04
BIDDING | 2026-05-01 | Architecture | Demolition Scope | Is GC or Plumber responsible for demo of plumbing in classrooms? Same for Electric & HVAC Duct. | Each contractor is responsible for demolition as detailed in the contract documents. | 2026-05-04 | Architecture (FS)
BIDDING | 2026-05-01 | CCAC | Freight Elevator | Is there a freight elevator available for Contractor use? | No freight elevator. Use passenger elevator in south wing or use a lift to a window within the lab space. | 2026-05-05 | CCAC (MP)
BIDDING | 2026-05-01 | CCAC | Sign-In Sheets | Please provide a copy of sign in sheets. | Sign in sheets provided in Addendum 01 on 05/01/2026 | 2026-05-01 | CCAC
BIDDING | 2026-05-01 | CCAC / Electrical | LV Bids | Are Low Voltage bids going to the Electrical Contractors? | Yes, low voltage is in the Electrical Contractor's scope of work. | 2026-05-05 | Architecture (FS)
BIDDING | 2026-05-01 | Electrical / LV | TR Room Location | Provide information on the Tele/Data Room location that the Low Voltage cabling will originate. | LV: See drawing E301, Communications General Note 5 - Coordinate Telecom Room location w/ local CCAC representatives. Refer to attached plans for server room location. | 2026-05-05 | Low-V: DS
BIDDINGA38:J38 | 2026-05-01 | CCAC / Electrical / LV | Data Racks | Provide picture of existing Tele/Data racks. | LV: See drawing E301, Communications General Note 5 - Coordinate Telecom Room location w/ local CCAC representatives. | 2026-05-05 | Low-V: DS
BIDDING | 2026-05-01 | CCAC / LV | LV Cable Type | What type of cable for this installation? CAT-6 or CAT-6A and any preferred Manufacturer? | LV: See drawing E404, Detail 1 and E502 schedules - Category 6A cabling. CCAC to respond with manufacturer preferences, unless noted otherwise. | 2026-05-05 | Low-V: DS
BIDDING | 2026-05-01 | Electrical | Add Alternate Single Line Diagram | In reference to the alternate for this project, can a single line diagram be issued on how we are to wire the key switches, it appears that there are 15 circuits which would need a shunt trip breaker for each receptacle circuit involved at the panels. Would we need a keyed switch for each circuit? | Each room will be controlled individually so there would be one key switch controlling multiple contactors (either one for each circuit or multi-poke contactors with separate contact sets). | 2026-05-04 | Electrical (TD)
BIDDING | 2026-05-01 | Mechanical | Existing Risers | Drawing M-111, we are tying into existing risers do you know what size they are? The first branch off is an unknown size and they look as if they are going down, can you verify please? | It depends where it is deemed possible to connect to the largest mains in the mechanical room, and the branch off is (4) 1-1/4" drain lines. | 2026-05-05 | Mech (BG)
BIDDING | 2026-05-04 | CCAC | Staging | Where will our lay down area be located? Where will we be able to stage a dumpster? Is there a freight elevator that will be available to contractors? | Dumpsters and laydown area per attached document from CCAC Facilities. No freight elevator exists. Use passenger elevator in south wing or use a lift to a window within the lab space. | 2026-05-05 | CCAC (MP)
BIDDING | 2026-05-04 | Architecture | 5th Floor Above Ceiling Work | Which trade will be responsible for the ACT removal and replacement on the Fifth Floor? Will containments be required and if so who is responsible for their construction and maintenance? | Refer to General Coordination Notes on AD102: Each contractor is responsible for removal and replacement of existing ceiling tiles and fixtures as required to perform wok. The GC is responsible for the dust containment enclosure at each phase of work. In addition to drawing notes, each contractor is responsible for any required patching and firestopping as a result of their own work. | 2026-05-04 | Architecture (FS)
BIDDING | 2026-05-04 | LV / Electrical | Cables | How many cables to a half shaded triangle? | LV: See drawing E404, Detail 1 | 2026-05-05 | Low-V: DS
BIDDING | 2026-05-04 | Mechanical / Plumbing | Ceiling Plenum | Is the ceiling of the fifth and sixth floors return air plenum? If the ceiling of the sixth floor is return air plenum, which specification do we use for the DI Water system | The 6th floor does not have a return plunum. The 5th floor is unknown. | 2026-05-05 | Mech (BG)
BIDDING | 2026-05-04 | CCAC | MBE / WBE Requirement | Page 15/732 states a goal of 15% MBE/WBE. Page 26/732 ( General Conditions para 6) states a goal of 13% MBE & 7% WBE. Which goal is correct? | The 20% goal is applicable – 13% MBE and 7% WBE. | 2026-05-04 | CCAC Mike Cvetic
BIDDING | 2026-05-04 | Architecture | Classroom Board Install | On drawing E502 there are several items that are owner furnished contractor installed including 4x4 ceramic white boards, 6x4 ceramic white boards, and 86" Interactive displays. Whose responsibility is it to install these items the GC or EC? | GC shall install the Interactive displays and white boards. The EC shall provide all necessary power and data for a complete installation. | 2026-05-05 | Architecture (FS)
BIDDING | 2026-05-04 | Electrical | Distribution Panel | PLEASE PROVIDE EITHER A LOCATION DRAWING OR THE DISTANCE FOR THE NEW FEEDERS COMING FROM DISTRIBUTION PANEL #2 TO THE NEW PANELS D & E | Distribution panel #2 is located in room 416. Refer to floor plans provided in Addendum. | 2026-05-06 | Architecture (FS)
BIDDING | 2026-05-04 | Electrical | Distribution Panel | PLEASE PRODIVE EITHER A LOCATION DRAWING OR THE DISTANCE FOR THE NEW FEEDER COMING FROM DISTRIBUTION PANEL #2 TO DOAS-1 | Distribution panel #2 is located in room 416. Refer to floor plans provided in Addendum. | 2026-05-06 | Architecture (FS)
BIDDING | 2026-05-04 | Electrical | Fire Alarm Vendor | PLEASE PROVIDE NAME & CONTACT FOR THE FIRE ALARM VENDOR AT THE CAMPUS
BIDDING | 2026-05-04 | Electrical | MC Cable | IS MC CABLE ACCEPTABLE FOR BRANCH CIRCUITS OR MUST EVERYTHING BE DONE IN EMT ? | MC cable for branch circuit can be used provided it meets appplicable NEC requirements. Coordinate with AHJ for final approval. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-04 | Electrical | MC Cable | IS MC CABLE ACCEPTABLE AS FIXTURE WHIPS ABOVE CEILINGS? | MC cable for branch circuit can be used provided it meets appplicable NEC requirements. Coordinate with AHJ for final approval. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-04 | Electrical | Emergency Lighting | LIGHTING GENERAL PLANS NOTE#3 MENTIONS THE USE OF AN UL924 TRANSFER DEVICE FOR ALL EM FIXTURES ON EM GENERATOR CIRCUIT. ALL OF THE R-1E FIXTURES HAVE AN INTEGRAL BATTERY BACK UP IN THE FIXTURE AND ARE FEED FROM PANEL E WHICH IS NOT AN EMERGENCY PANEL. PLEASE PROVIDE MORE INFORMATION ON INTENT OF GENERAL NOTE #3 | General note will be revised. See Addendum #3 drawings. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-04 | Electrical | Equipment | GENERAL NOTE #2 REFERENCES CORD PLUG ENDS FOR EQUIPMENT IN THIS AREA. PLEASE PROVIDE EQUIPMENT SCHEDULE THAT DEFINES COUNTS AND NEMA CONFIGURATIONS. | There is no specity equipment. General note will be revised. See Addendum #3 drawings. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-04 | Architecture | Furred Walls | THERE WAS MENTION AT THE WALK THRU THAT THE WALLS IN FRONT OF PANELS E & D WILL BE FURED OUT FOR THE INSTALLATION OF THE NEW PANELS E&D THAT ARE BEING INSTALLED. CAN THAT PLEASE BE CONFIRMED? | New panels are in same location as existing panels.No wall furring is included at this time. | 2026-05-05 | Architecture (FS)
BIDDING | 2026-05-04 | CCAC/Architecture | Phasing | WILL THE LABS BE FULLY SHUT DOWN DURING CONSTRUCTION? | The labs will be unoccupied during construction. Refer to sheet G102 for project phasing, access requirements to existing toilet rooms, corridor, and stairs. | 2026-05-05 | Architecture (FS)
BIDDING | 2026-05-04 | CCAC | 5th Floor Above Ceiling Work | GENERAL NOTE #3 UNDERFLOOR WORK. STATES THAT ALL WORK UNDERFLOOR IS THE BE SCHEDULED ON SUMMER BREAKS, HOLIDAYS & OR WEEKENDS. CAN YOU PLEASE PROVIDED WHEN THE SCHOOL BREAKS BEGIN AND END AS WELL AS ANY HOLIDAYS THAT WERE MENTINONED | The scheduling of the work will be coordinated with the contractor(s) once they are on board. | 2026-05-06 | CCAC (NK)
BIDDING | 2026-05-04 | CCAC | MBE / WBE Requirement | THE BID FORM 1148 ELECTRICAL MBE/WBE PARTICIPATION STATES 15% WHEREAS GENERAL CONDITIONS PARAGRAPH 6 STATES 20% 13% MINORITY & 7% WOMAN. CAN YOU PLEASE CLAIRFY WHICH ONE IS CORRECT? | The 20% goal is applicable – 13% MBE and 7% WBE. | 2026-05-05 | CCAC (MC)
BIDDING | 2026-05-04 | Electrical | Light Fixtures | LIGHTING SCHEDULE IS CALLING OUT LITHONIA LIGHT FIXTURES. CAN WE USE AN APPROVED EQUAL FOR LIGHT FIXTURES AND EXIT SIGNS BIENG THAT REPCOII HAS THE CURRENT LIGHTING CONTROL PKG IN THE BLDG? | Lithonia lights can be replaced with those specified in RepcoII lighting package. See addendum #3 drawings for update. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-04 | CCAC / Mechanical | DDC System | It says that a JCI Metasys is the only accepted DDC manufacture/system. Would CCAC be willing to accept ALC as an alternative if we could integrate back into the existing JCI system using BACnet? *Clarification Request: On Sheet 230923-36, Spec Sec. 3.2, It says "DDC System Interface with Existing Siemens BAS." Is the existing system in fact Siemens or is it JCI Metasys? | Existing System is JCI Metasys, and the owner has instructed us not to allow alternates. | 2026-05-05 | Mech (BG)
BIDDING | 2026-05-05 | Electrical | Fire Alarm Symbols | 1. Fire alarm notification devices shown on drawing FA101 and symbols shown on E001, indicate horns, strobes, speaker strobes and horn speakers. Please clarify which is correct. Is project to be a voice evacuation fire alarm system or evacuation via audible horns. Also is there a symbol for a stand alone strobe? 2. Please name the manufacturer of the existing fire alarm system. | Sheet FA101 is showing speaker strobes, and strobes only. There are no horn shown. See addendum #3 drawings for strobe symbol. The existing FA manufacturer is Simplex. Coordinate with AHJ of the system is a vioce evacuations system or audible horns. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-05 | CCAC | Bonds | 1. Project start and finish dates June 2026 through substantial completion 4-2-27. 2. Any Maintenance Period 3. Liquidated Damages/Penalties | 1) June 2026 through substantial completion 4-2-27. 2) N/A 3) There are liquidated damages in the A101 of $500 per day. | 2026-05-05 | CCAC (MC)
BIDDING | 2026-05-05 | Electrical | Liquidated Damages | Is there any Liquidated Damages for this project? | There are liquidated damages in the A101 of $500 per day. | 2026-05-05 | CCAC (MC)
BIDDING | 2026-05-05 | Architecture | Floor-to-Floor Heights | What is the existing floor-to-deck height within the area(s) scheduled to be renovated? | The roof deck is approximately 14'-8" above the 6th floor level. Verify in field | 2026-05-05 | Architecture (FS)
BIDDING | 2026-05-05 | Architecture | 5th Floor Above Ceiling Work | The fifth floor plumbing demo/installation will require the ACT ceilings to be opened for access. During the pre-bid meeting walk through it was stated that the GC will be resposible for the removal and replacement of the ACT ceilings for the plumbing and electrical work on the fifth floor. Can you please verify that this work will be required to be done by the GC. | Refer to General Coordination Notes on AD102: Each contractor is responsible for removal and replacement of existing ceiling tiles and fixtures as required to perform wok. The GC is responsible for the dust containment enclosure at each phase of work. In addition to drawing notes, each contractor is responsible for any required patching and firestopping as a result of their own work. | 2026-05-05 | Architecture (FS)
BIDDING | 2026-05-05 | Architecture | Fixture Scope | Under the GC Summary, it states "GC to provide laboratory casework and associated plumbing fixtures, Installation of associated plumbing fixtures by Plumbing Contractor". On drawing P001, in the plumbing fixture schedule, it shows the PC is to provide the faucets for the S-1 & S-2. Please confirm that the GC is to provide and install the counter top (with integral sink bowl) and the PC is to provide and install the faucets and additional items mentioned in the plumbing fixture schedule. | GC shall purchase the lab sinks and faucets as part of the lab casework package. The GC shall install the sink with the lab countertops. The PC shall provide all components not included in the casework package and shall install all faucets, drains, plumbing lines, and any remaining components necessary for a complete system. | 2026-05-06 | Architecture (FS)
BIDDING | 2026-05-05 | Plumbing | Acid Waste and Vent | Under the sanitary waste and vent piping, there are no specifications for the acid waste and acid vent piping. Can you please add these specifications to the next addendum? | Section 221300 will be added in addendum | 2026-05-04 | Plumbing (SW)
BIDDING | 2026-05-05 | Plumbing | DI Water | Under the Processed Water Systems section there are no specifications for the DI System equipment. Is the equipment being supplied by others (CCAC) or the PC? If by the PC, can you distribute the specifications in the next addendum? Also, if it is being supplied by others, will the PC be expected to install it? | The DI system is a delegated design and shall be provided by the PC. Provide Type II water quality for the locations noted in the documents. | 2026-05-12 | Plumbing (SW)
BIDDING | 2026-05-05 | Electrical / LV | Access Control | For Access Control - what is the current manufacturer? Is the intent to reuse the access control equipment being removed from the eight existing doors? | LV: See drawing E301, Communications General Note 10 and 11. The Contractor is responsible for coordianting with local CCAC representatives and evaluate existing systems, including potential reuse of devices. | 2026-05-08 | Low-V: DS
BIDDING | 2026-05-05 | Electrical | Lighting Controls | Keynote 2 on drawings E101: calls for existing switches to be reinstalled and programmed. From my understanding, these lighting controls have been discontinued and programming them poses a major challenge, due to a limited amount of personnel with the skillset. Please advise. | All notes have been revised. See Addendum #3 drawings for update. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-05 | Electrical | Light Fixtures | Drawing E101: Are R1E fixtures to be furnished new or are we retrofitting existing 2x4 fixtures with a backup battery? Fixtures schedule calls for flat panels, existing fixtures are troffer style. Please advise. | All notes have been revised. See Addendum #3 drawings for update. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-05 | Electrical | Light Fixtures | Drawings E101: Keynote 1 calls for type R1 fixtures to be reused, however the fixture schedule calls for flat panels but the existing fixtures are troffer style. Please advise. | All notes have been revised. See Addendum #3 drawings for update. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-05 | Electrical | Emergency Lighting | Drawing E101 Gen Note 2-3: There is currently an emergency lighting circuit serving the space that is powered by the generator. Is the use of the batteries (Type R1E fixtures) to eliminate the existing emergency circuit? General notes 2 and 3 seem to contradict how emergency power is provided to these fixtures, as panels E and D are not tied to emergency power. | all emergency lights are to have integral battery and not connectec to generator power. General notes 2 and 3 have been updated. See Addendum #3 drawings for updates. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-05 | Electrical | Panel | Please provide manufacturer and model of distribution panel #2. | manufactuer is General Electric | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-05 | Electrical | Panel Location | Please provide location of distribution panels #2 and #3. | Distribution panel #2 is located in room 416 and Distribution panel #3 is located in room 549. Refer to floor plans provided in Addendum. | 2026-05-06 | Architecture (FS)
BIDDING | 2026-05-05 | Electrical | IT Location | Please provide location of IT room. | Refer to attached plans for server room location. | 2026-05-06 | Architecture (FS)
BIDDING | 2026-05-05 | Electrical | Lighting Controls | Specifications call for nlight controls, however these are not compatible with the existing wattstopper controls in the building. Please advise. | Lighting controls is to be Wattstopper. Specifications will be updated | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-05 | Electrical | Lighting Panel Location | Where is the existing Lighting control panel located? | Coordinate location with COR personnel. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-05 | CCAC | Labor Participation | The Project Labor Agreement requires the general contractor and all subcontractors to provide only union labor for this project, effectively preventing non-union contractors from bidding or working on the project, which limits the pool of MWDBE companies able to participate on this project. Though the Labor Stabilization Agreement states non-union contractors can be used on the project, they will have to work with the union and provide union labor, essentially signing on with the union. Please confirm this will be taken into consideration when reviewing good faith efforts in case of the event that the participation goals cannot be attained. Additionally, there are contradicting participation goals in the spec. Return Form 4.0 states 15% overall but section 6 of the General Conditions states 20%. Please advise which is correct. |  | 2026-05-12 | CCAC (MC) | This will be taken into consideration when evaluating the good faith effort. Also, be reminded that the purchase of supplies/materials used for the project from MWDBE firms will be considered. The 20% goal is applicable – 13% MBE and 7% WBE.
BIDDING | 2026-05-06 | Electrical | Panel Location | 1. E602 - Please provide a floor plan showing locations of DIST. PANEL #2 and DIST PANEL #3. This is necessary to assess the feeders to the new panels (D and E) and to DOAS-1. | Distribution panel #2 is located in room 416 and Distribution panel #3 is located in room 549. Refer to floor plans provided in Addendum. | 2026-05-06 | Architecture (FS)
BIDDING | 2026-05-06 | Low Voltage | Data Cables | HOW MANY DATA CALES GO TO EACH LOCATION? THERE IS NOTHING NOTED ON THE LEGEND. | LV: See drawing E404, Detail 1 | 2026-05-08
BIDDING | 2026-05-06 | Low Voltage | TR Room Location | WHAT IT CLOSET SHOULD THE NEW DATA CABLES BE RAN TO? | LV: See drawing E301, Communications General Note 5 - Coordinate Telecom Room location w/ local CCAC representatives. | 2026-05-08 | Low-V: DS
BIDDING | 2026-05-06 | Low Voltage | Cabling | ELECTRICAL DEMO GENERAL NOTE #10 STATES THAT ALL OF THE EXISTING DATA CABLE MUST BE PULLED BACK TO IT CLOSET FOR RE-USE BUT THE EXISTING CABLE IS CAT 6 AND THE DRAWINGS ARE CALLING FOR CAT-6A FOR NEW DATA DROPS. PLEASE ADVISE ON WHICH ONE IS CORRECT? | LV: Existing cabling to be reused to the extent possible. New cabling to be Cat 6A | 2026-05-08 | Low-V: DS
BIDDING | 2026-05-06 | Low Voltage | Security | WHO IS RESPONSIBLE FOR THE SECURITY SHOWN ON DRAWING E-301, AND WHAT SECURITY VENDOR NEEDS TO BE USED TO BE COMPATABLE WITH THE CCAC CAMPUS? | LV: See drawing E301, Communications General Note 10 - Coordinate systems location w/ local CCAC representatives. Per note 10 and 11, The Contractor bidding on the work is responsible for tying into the existing system. | 2026-05-08 | Low-V: DS
BIDDING | 2026-05-06 | LV / Electrical | Floor Outlet | THE PLANS AND SPECS DO NOT CALL FOR A SPECIFIC FLOOR BOX FOR ELECTRICAL AND DATA. PLEASE PROVIDE MANUFACTURE AND MODEL NUMBER OF BOX THAT IS REQUIRED? | LV: Provide Wiremold RC7AFFTCAL poke-thru for electric, drawing sheet E401. Provide Wiremold poke-thru w/ 1-1/2" raceway for LV, drawing sheet E402. | 2026-05-08 | Low-V: DS
BIDDING | 2026-05-06 | Electrical | Panel Conduits | 2. E602/Note 1 - This note states to use existing conduit to extent possible. Please confirm the existing raceways for this note on feeders to Panel 'E' and Panel 'D' are 2" and 3" respectively. Is the path of these raceways known and if so, can it be provided? | Per the existing riser diagram we have on hand. Yes, they are 2" and 3" respectively. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-06 | Electrical | Feeders / Raceway | 3. E602/Note 5 - Only pulling a new feed is mentioned to panel DD and not new conduit. Based on other notes on this page is the intent to also provide a new raceway or only new feeder in existing raceway? | yes, new feeder only in existing conduit. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-06 | Electrical | Spares Locations | 4. Spec 262416,3.1,I - Please confirm the requirement of these (4) additional 1" spares to above ceiling per panel only applies to new Panels D and E.
BIDDING | 2026-05-06 | Electrical | DOAS Label | 5. M702 - RTU-155 is not shown on the electrical drawing nor the mechanical drawings. Are these notes supposed to be for the DOAS-1? If not, please provide notes for DOAS-1 specifically, if VFD or means of disconnect is being provided for EC to install or if EC is to Furnish and install; and any required info if so. | RTU-155 was a previous tag for DOAS-1. Only one AHU is to be provided (DOAS-1). VFDs and disconnects are to be provided and installed by the EC. | 2026-05-08 | Mechanical (TC)
BIDDING | 2026-05-06 | Electrical | Light Fixtures | NOTE#1 ON E-101 STATES THAT ALL TYPE R-1 FIXTURES ARE EXISTING AND TO BE RE-INSTALLED BUT E-501 ON THE LIGHTING FIXTURE SCHD CALLS FOR NEW TYPE R-1 FIXTURES. ALSO, THE EXISTING R-1 FIXTURE IS A COMPLETELY DIFFERENT FIXTURE THAN THE TYPE RE-1 THAT WE ARE TO INSTALL. PLEASE ADVISE WHICH IS CORRECT? | All notes have been revised. See Addendum #3 drawings for update. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-06 | Electrical | Wattstopper | NOTE #8 STATES THAT ALL FIXTURES AND ASSOCIATED LIGHTING CONTROL IS TO BE COMPATABLE WITH WATT STOPPER PLUS. WHICH WILL INCLUDE ALL SENSORS, CONTROL DEVICES, LED DRIVERS, MODULES AND ASSOCIATED INTERFACING COMPONENTS TO ALLOW CONNECTION WITH THE EXISTING BUILDING SYSTEM. IT ALSO GOES ON TO MENTION THAT THERE CAN BE NO WIRELESS DEVICES INSTALLED, YET THE WATT STOPPER PLUS IS A WIRELESS SYSTEM. PLEASE PROVIDE A RISER DIAGRAM SHOWING DEVICES NEEDED AND INTENT OF CONTROL..PLEASE ALSO MAKE NOTE, THE CURRENT FIXTURE TYPE R-1 & TYPE RE-1 AS SHOWN ON THE FIXTURE SCHEDULE IS NOT COMPATABLE WITH THE WATT STOPPER PLUS LIGHTING CONTROL PROGRAMMING. | All notes have been revised. See Addendum #3 drawings for update. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-06 | CCAC | Schedule | PLEASE PROVIDE START AND DURATION FOR THE PROJECT. | June 2026 through substantial completion 4-2-27. | 2026-05-06 | CCAC (MC)
BIDDING | 2026-05-06 | CCAC | Bid Extension | WE ARE REQUESTING AN EXTENSION OF THE BID DATE DUE TO THE NUMBER OF THE QUESTIONS WE HAVE AND TO GIVE US ADEQUATE TIME AFTER RFI'S ARE ANSWERED TO IMPLEMENT RESPONSES. |  | 2026-05-07 | CCAC (NK) | The due date has been extended to Friday, May 15, 2026 at 2:00 p.m.
BIDDING | 2026-05-06 | Mechanical | Panels | Are perforated panels required for fan sections only, or every section in the unit? | Perforated panels are required for all sections of the DOAS. | 2026-05-07 | Mech (TC)
BIDDING | 2026-05-06 | Mechanical | Coating | Could you please provide more information on the microbial coating requirement for the inside casing wall? | Strike specifications section 2.3 C. 2. c. from the requirements of the DOAS. The antimicrobial coating will NOT be required. | 2026-05-07 | Mech (TC)
BIDDING | 2026-05-06 | Mechanical | Unit Dimensions | Could you please advise on the max weight, length, and height of the unit? | Refer to the Dedicated Outdoor Air System schedule on M702 for max size and weight. | 2026-05-07 | Mech (TC)
BIDDING | 2026-05-06 | Mechanical | Supply Fans | Please advise on the number of supply fans. | 2 supply fans in the DOAS. | 2026-05-07 | Mech (TC)
BIDDING | 2026-05-06 | Mechanical | Bypass Dampers | Are internal bypass dampers acceptable in lieu of integral bypass dampers? | Internal bypass dampers will be an acceptable substitution for IFB dampers | 2026-05-07 | Mech (TC)
BIDDING | 2026-05-06 | Mechanical | Unit Orientation | What is the orientation of DOAS-1? The plans show vertical, but the spec states horizontal. | Horizontal. | 2026-05-07 | Mech (TC)
BIDDING | 2026-05-06 | Mechanical | Unit Layout | Could a detailed layout of DOAS-1 be provided? | No addendum will be provided. Please follow the DOAS schedule and specifications section 237433 for specific requirements of the DOAS. | 2026-05-07 | Mech (TC)
BIDDING | 46148 | Mechanical | Exhaust Ductwork | The sheet metal material spec says to use 316 SS for ductwork connected to fume hoods. The duct specs do not indicate if the indoor fume hood duct should have welded joints. Please advise if the fume hood exhaust duct should have welded or flanged joints. | Please include welded joints for fume hood exhaust | 2026-05-06 | Mech (BG)
BIDDING | 2026-05-07 | Architecture | Dust Enclosures | General Coordination Note #3 & 4 - All primes to provide a phasing plan for approval. General Contractor to provide dust protection for work by the primes on the 5th floor for each phase. As a General Contractor, how are we to know how large of an area that we need protection to provide for each phase when the phases have not been determined yet? We'll have to install and take down for each phase. How many phases are we to include? | The work will have to be planned between the Prime Contractors and CCAC as stated in the contract documents. | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 | Architecture | Coordination of Work | Who is responsible for coordination between trades? In one section is says the owner will be responsible but in the General Construction scope it lists coordination between trades as being on the GC. | The GC is responsible for coordination of trades. | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 | Low Voltage | Cable Demoliton | Print ED 102 (4-14-2026) per Electrical Note #10 --- Are we to assume that all cables noted will be back pulled and then re pulled back into renovated area for re use? This question applies to the AP cables, card access cables and the voice/data cables. | LV: Existing cabling to be reused to the extent possible. | 2026-05-08 | Low-V: DS
BIDDING | 2026-05-07 | Architecture | OFCI Equipment | Please clarify which contractor(s) will be responsible for OFCI equipment | LV: The Contractor bidding on the work is responsible for installing Owner furnished equipment s noted on drawings. | 2016-05-08 | Low-V: DS
BIDDING | 2026-05-07 | CCAC | Award Date | What is the anticipated award date? |  | 2026-05-12 | CCAC (MC) | Anticipated award date is just after the June 4, 2026 Board meeting.
BIDDING | 2026-05-07 | CCAC | Start Date | What is the anticipated start date? | 2026-06-01 | 2026-05-07 | CCAC (MC)
BIDDING | 2026-05-07 | Architecture | New Roof | What type of roofing system will be installed during the upcoming roof replacement project? | Refer to Roof Plan on sheet A121 | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 | CCAC | New Roof Install | When is the new roofing system anticipated to be installed? | Concurrent with this project | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 | Architecture | Schedule | Section 13200 B. Related Requirements: states Reference Section 011000 “Summary" for preparing a combined Contractor's Construction Schedule. Section 011000 has references to the contractor preparing schedules but does not appear to have anything referencing a combined schedule. Who is responsible for creating a combined schedule? | The GC is responsible. | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 | CCAC | Laydown Area | Where will the contractors be allowed to have their laydown yard for dumpster and materials staging? | Refer to attached plan from CCAC. | 2026-05-07 | CCAC (MC)
BIDDING | 2026-05-07 | Architecture | Roof Walkway Pads | Sheet A121 Construction Key Note 7.08 states “Provide new Membrane Walkway Pads, Adhered to Roof Membrane”. During the walkthrough it was noted that this work would likely be done before the new roof was completed. Please confirm if the contractors bidding should provide these or if the contractor installing the new roof will be providing the walkway pads? | Refer to General Note 6 on sheet A121. | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 | Electrical | Fire Alarm System | Can you provide the manufacturer of the existing Fire Alarm System? | Manufactuer is Simplex | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-07 | Electrical | Roof Penetrations | Will roof penetrations for electrical conduits be furnished and installed by the roofer or will there be a cost to the electrical contractor for these? | Installed by EC | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-07 | Electrical | Fire Alarm Devices | Is the electrical contractor responsible to provide the devices, equipment and programming for the security devices as shown on E301 or are we to provide conduit, backboxes and cabling only? If components are required who is the system vendor for the building? | LV: See drawing E301, Communications General Note 10 and 11 - The Contractor bidding on the work is responsible for providing devices and tying into the existing system. | 2026-05-10 | LV: DS
BIDDING | 2026-05-07 | Architecture | Interactive Displays | Is the Electrical contractor responsible to install the display monitors and the associated mounting hardware? | GC shall install the Interactive displays. The EC shall provide all necessary power and data for a complete installation. | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 | Architecture | Wall Blocking | Will the GC furnish wall blocking where required for display mounting? | GC will furnish blocking per notes on A401 and A402 | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 | Architecture | OFCI Equipment | Which prime is responsible for mounting the whiteboards listed in the OFCI Schedule on E502? Can you provide a breakdown of which prime is responsible for each of the OFCI items? | GC shall install the white boards.The EC is responsible for installation of the ceiling mounted speakers, cameras, and mic | 2026-05-07 | Architecture (FS)
BIDDING | 2026-05-07 | Low Voltage | Faceplates | Will the faceplates shown in the details on E403 be provided by the AV vendor? | LV: See drawing E502 for Owner furnished materials | 2026-05-10 | LV: DS
BIDDING | 2026-05-07 | Electrical | Fire Alarm Devices | On Drawing FA101, the Partial Sixth Floor Fire Alarm Plan, the Fire Alarm System Notification Appliances are identified as Speaker/Strobes and unless this has changed, our records indicate that the Fire Alarm Notification Appliances are Horn/Strobes installed in 2003. Can you please confirm that Speaker/Strobes or Horn/Strobes are required? | the existing system is horn/strobes. See Addendum #3 for drawing updates. | 2026-05-13 | Electrical (TD)
BIDDING | 2026-05-07 | Electrical | Fire Alarm System | Has the Fire Alarm System in the building been “Updated” since 2003 when it was installed? If not, does the building owner understand that the existing Fire Alarm System is the old and obsolete Siemens MXL with only “Used” and “Refurbished” Parts available for it?
BIDDING | 2026-05-08 | Plumbing | DI Water | Please provide the following information: The spec on the drawing: “Aqua Solutions Type II Reagent Grade DI Water System or Equal test current water quality and provide a system to deliver Type II water quality at 20 LPM.” We just received the following response from Aqua Solutions: Aqua Solutions does not manufacture a water purification system which will meet your requirement of 20 Liter per minute flow rate to 6 dispensing points across a large lab. Our systems are primarily point of use. Please advise. | The diagram on P501 details the components required for a centralized DI water system. The ELGA Labwater R60/R120 system or a comparable system is acceptable. | 2026-05-12 | Plumbing (SW)
.